## Slide 1
Role of Indian Electricity Grid Code
For
Reliable Secure and Economic Dispatch of Power
Regulatory and Consumer Point of View
R.K.Bansal (Ex General Manager)
POWERGRID

## Slide 2: Consumer point of view
Consumer
  24X7 safe secure quality supply at affordable price
  Dispute free metering billing collection
  Ease of connection disconnection
  Standard operating procedures, supply codes
  Performance measurement
  Net metering to facilitate solar power
  Redressal mechanism
  Transparent web based platforms
  DISCOM, DERC the enablers

## Slide 3: Regulatory point of view
Regulators established under EA 2003
  CERC at central level
  SERC and JERCs for States and Uts
to regulate the tariff of inter-state generating companies
to regulate the inter-State transmission of electricity
to determine tariff for inter-State transmission
to issue licenses for inter state electricity transmission and trading.
to adjudicate upon inter-State disputes
to specify Grid Code
to specify and enforce the standards with respect to quality, continuity and reliability of service
to fix the trading margin ( only CERC)

## Slide 4: Background
First Grid Code was prepared in 1999
The Grid Code was re-notified in 2006 and again in , 2010.
  The Grid Code 2010 was amended from time to time to address requirements of the sector.
  CERC notified six amendments in the Grid Code 2010.
  The major amendments were related
    to inclusion of forecasting,
    scheduling framework for renewable generation,
    compensation for part load operation of thermal stations for absorbing renewable energy
    and procedure for declaration of commercial operation date.
All India installed generation capacity 89 GW to 360 GW in Dec 2019
Present renewable capacity 82 GW
Annual all India electricity generation has trebled to 1250 billion units
The average renewable energy penetration in the order of 9%
Expected to cross 20% in the few next years.
Renewable rich states are finding it difficult to manage renewable generation during high renewable generation season.
Grid operators trying to manage the variability and intermittency of solar and wind generation with minor innovations such as asking the solar and wind generators to forecast their output and backing down thermal units during high renewable season.
Constitution of expert Group by CERC for Review of IEGC
Report submitted by the Group along with draft IEGC 2020

## Slide 5: Preamble of Draft IEGC 2020
The preamble has been redrafted to reflect focus on reliable Grid operation and integration of renewable energy as follows:
…. The IEGC lays down regulations to be followed by various persons and participants to plan, develop, maintain and operate power system in the country in a secure, economic, reliable, resilient and efficient manner. The regulations provide for integration of renewable energy resources in the grid, flexible operation of energy resources, optimum scheduling & despatch, open access, promoting competition in the generation sector and various measures including reserves necessary for grid stability. It seeks to create a robust framework for maintaining demand-supply balance under credible contingencies and an enabling framework for transition to clean energy sources. According to clause (h) of sub-section (1) of Section 86, the State Commission shall specify its state grid code consistent with the IEGC.

## Slide 6: Outline of the presentation
IEGC 2010
IEGC 2020

## Slide 7: INDIAN ELECTRICITY GRID CODE 2010
Applicable w.e.f. 3rd May,2010

## Slide 8: IEGC - INTRODUCTION
The Indian Electricity Grid Code (IEGC)
Regulation made by the Central Commission
In exercise of powers under clause (h) of subsection (1) of Section 79 read with clause (g) of sub-section (2) of Section 178 of the Act.

## Slide 9: What is IEGC ?
A Set of rules, guidelines and standards
  to be followed by various persons and participants in the system
  to plan, develop, maintain and operate the power system,
  in the most secure, reliable, economic and efficient manner,
  To facilitate healthy competition in the generation and supply of electricity

## Slide 10: INDIAN ELECTRICITY GRID CODE 2010
IEGC Feb 2000
IEGC Mar 2002
IEGC April 2006
IEGC April 2009
IEGC April 2010

## Slide 11: OBJECTIVE of IEGC
The IEGC brings together a single set of technical and commercial rules, encompassing all the Utilities connected to/or using the inter-State transmission system (ISTS) and provides the following:
• Documentation of the principles and procedures which define the relationship between the various Users of the inter-State transmission system (ISTS), National Load Despatch Centre, as well as the Regional and State Load Despatch Centers
• Facilitation of the optimal operation of the grid, facilitation of coordinated and optimal maintenance planning of generation and transmission facilities in the grid and facilitation of development and planning of economic and reliable National / Regional Grid
• Facilitation for functioning of power markets and ancillary services by defining a common basis of operation of the ISTS, applicable to all the Users of the ISTS.
• Facilitation of the development of renewable energy sources by specifying the technical and commercial aspects for integration of these resources into the grid

## Slide 12: Structure of IEGC
IEGC contains the following:
i) Part 2: Role of various Organizations and their linkages
This Part defines the functions of the various Organizations as are relevant to IEGC.
ii) Part 3:Planning Code for inter-State transmission
This Part provides the guidelines to be adopted in the planning and
development of bulk power transfer and associated ISTS. The
Planning Code lays out the detailed information exchange required
between the planning agencies and the various participants of the
power system for load forecasting, generation availability, and
power system planning etc. for the future years under study. The
Planning Code stipulates the various criteria to be adopted during
the planning process

## Slide 13: Structure of IEGC
iii) Part 4: Connection Code
This Part specifies minimum technical and design criteria to be
complied with by STU, CTU and any User connected to the system
or seeking connection to the ISTS, to maintain uniformity and
quality across the system. This also includes procedure for connection to the ISTS
iv) Part 5: Operating Code
This Part describes the operational philosophy to maintain efficient,
secure and reliable Grid Operation and contains the following
sections.
(a) Operating Philosophy
(b) System security aspects
This section describes the general security aspects to be
followed by generating companies and all Regional Entities,
CTU, STU, and all other Users of the Grid.

## Slide 14: Structure of IEGC
(c) Demand Estimation for operational purposes
This section details the procedures to estimate the demand
by the SEB/distribution licensees for their systems / SLDCs
in their control area for the day/week/month/year ahead,
which shall be used for operational planning.
(d) Demand management
This section identifies the methodology to be adopted for
demand control by each SEB/SLDC/Distribution Licensee/
bulk consumer depending on, overdrawal by the entity,
frequency, voltage and transmission congestion. and any
other requirement of grid security.
(e) Periodic Reports
This section provides various provisions for reporting of the
operating parameters of the grid such as frequency profile etc.

## Slide 15: Structure of IEGC
(f) Operational liaison
This section sets out the requirement for the exchange of
information in relation to normal operation and/or events in
the grid.
(g) Outage Planning
This section indicates procedure for outage planning.
(h) Recovery procedures
This section contains the procedures to be adopted following
a major grid disturbance, for black start and
resynchronization of islands, etc.
(i) Event Information
This section indicates the procedure by which events are
reported and the related information exchange requirements
etc

## Slide 16: Structure of IEGC
v) Part 6: Scheduling and Despatch Code
This section deals with the procedure to be adopted for scheduling and Despatch of generation of the Inter-State Generating Stations (ISGS) and scheduling for other transactions through long-term access, medium-term and short-term open access including complementary commercial mechanisms, on a day-ahead and intra-day basis with the process of the flow of information between the ISGS, National Load Despatch Centre (NLDC), Regional Load Despatch Centre (RLDC), Power Exchanges and the State Load Despatch Centres (SLDCs), and other concerned persons .
Most of the wind and solar energy sources are presently connected and in future are likely to be connected to the STU or the State’s distribution utility. However, keeping in view the variable nature of generation from such sources and the effect such variability has on the inter- state grid, and in view of the large-scale integration of such sources into the grid envisaged in view of the Government of India’s thrust on renewable sources of energy, scheduling of wind and solar energy sources has been
incorporated in this Code.
vi) Part 7: Miscellaneous

## Slide 17: Non -compliance of IEGC
(i) RLDCs shall report to the Commission instances of serious or repeated violation of any of the provisions of the IEGC and incidences of persistent non-compliance of the directions of the RLDCs issued in order to exercise supervision and control required for ensuring stability of grid operations and for achieving the maximum economy and efficiency in the operation of the power system in the region under its control.
(ii) The Regional Power Committee (RPC) in the region shall also continuously monitor the instances of non-compliance of the provisions of IEGC and try to sort out all operational issues and deliberate on the ways in which such cases of non-compliance are prevented in future by building consensus. The Member Secretary RPC may also report any issue that cannot be sorted out at the RPC forum to the Commission.The RPC shall also file monthly reports on status of UI payment and installation of capacitors by states vis-à-vis the requirement/targets, as decided in the RPC.

## Slide 18: Non -compliance of IEGC
(iii) The Commission may initiate appropriate proceedings upon receipt of report of RPCs or RLDCs referred to in (i) and (ii) above respectively.
(iv) In case of non-compliance of any provisions of the IEGC by NLDC, RLDC, SLDC, RPC and any other person the matter may be reported by any person to the CERC through petition.
(v) Notwithstanding anything contained in these regulations, the Commission, may also take suo-motu action against any person, in case of non-compliance of any of the provisions of the IEGC.

## Slide 19: 2.7 Role of SLDC
SLDC’s apex body for integrated grid operation within the State :
(a) optimum scheduling and despatch
(b) monitor grid operations;
(c) keep accounts of electricity
(d) supervision and control over the intra-State transmission system
(e) secure and economic real time operations as per the State Grid Code.
(f) achieve the maximum economy and efficiency
(g) accord concurrence or NoC for Open access in ISTS involving a state utility
Every state entity to comply with the directions of SLDC
SLDC to comply with the directions of the RLDC

## Slide 20: 2.8. Role of STU (2.8.1 Sec 39 of the Act, 2003
(1) (a) intra-State electricity transmission;
(b) of planning and relating to intra-state transmission system
co-ordination with i) CTU ii) State Governments
iii) generating companies; iv) Regional Power Committees;
v) Authority; vi) licensees;
(c) to ensure development of an efficient, co-ordinated and economical system of intra-State transmission lines
(d) to provide non-discriminatory open access to its transmission system
(2) STU to to operate the SLDC until a Government company or any authority or corporation is notified by the State Government

## Slide 21: CONNECTION CODE
4.6.1 Reactive Power Compensation
STU and users to provide Reactive Power compensation and/or other facilities, close to the load points thereby avoiding the need for exchange of Reactive Power to/from ISTS and to maintain ISTS voltage within the specified range.
b) To provide additional reactive compensation as per RPC and RLDC
The Users and STUs shall provide information to RPC and RLDC regarding the installation and healthiness of the reactive compensation equipment on regular basis.
RPC shall regularly monitor the status in this regard.

## Slide 22: CONNECTION CODE
4.6.2 Data and Communication Facilities
All users, STU and CTU to provide to RLDC :
Reliable and efficient speech
data communication systems
Systems to telemeter power system parameter such as flow, voltage and status of switches/ transformer taps etc.
in line with interface requirements and other guideline made available by RLDC.
Establish data flow up to appropriate data collection point on CTU’s system,
provide the required facilities at their respective ends as specified in the Connection Agreement
4.6.5 Cyber Security
All utilities shall have in place, a cyber security framework to identify the critical cyber assets and protect them so as to support reliable operation of the grid.

## Slide 23: OPERATING CODE
All the users to
5.1 (d) comply with the directions of RLDC /SLDC to ensure integrated grid operation and for achieving the maximum economy and efficiency in the operation of the power system.
5.1 (g) Develop a set of detailed operating procedures for each state grid in consistent with IEGC
5.1 (h) The control rooms of the NLDC, RLDC, all SLDCs, power plants, substation of 132 kV and above, and any other control centres of all regional entities shall be manned round the clock by qualified and adequately trained personnel. Training requirements may be notified by the Commission from time to time, by orders.
5.2.(d) Intimate any tripping, as soon as possible, say within ten minutes of the event. The reason (to the extent determined) and the likely time of restoration shall also be intimated. All reasonable attempts shall be made for the elements’ restoration as soon as possible.

## Slide 24: Frequency Control
Operating Frequency Range revised - 49.5Hz to 50.2Hz
Action for curtailing over drawal to be initiated at 49.7Hz
No overdrawal when frequency is 49.5Hz or below
Frequency Linked despatch guidelines to be followed
All SEBs /distribution licensees shall abide by the demand management measures of the SLDCs and comply the directions of SLDC. Any non-compliance shall be reported by SLDC to RLDC
Automatic Load disconnection (Demand side Management) scheme shall be implemented by the State utilities before 01.01.2011

## Slide 25: Voltage Control
Generating units of above 50MW size shall have AVRs (Automatic Voltage Regulators) in operation and PSS (Power System Stabilizers) shall be got properly tuned.
Operating Range of Voltage |  | 
Nominal | Maximum | Minimum
765 | 800 | 728
400 | 420 | 380
220 | 245 | 198
132 | 145 | 122
110 | 121 | 99
66 | 72 | 60
33 | 36 | 30

## Slide 26: System Protection Schemes
AUFR / df/dt Schemes:
SLDC shall furnish the details of load relief on operation of AUFR or df/dt to RLDC on real time basis.
RLDC shall report such instances to RPC where there was no/inadequate response.
SLDC shall submit a monthly report to RPC in this regard
RLDC shall submit a comparative record of expected load relief and actual load relief obtained in Real time system operation to RPC and CERC on monthly basis.
SPS (SPECIAL PROTECTION SCHEMES) Shall be identified, installed and commissioned to operate the transmission system closer to its limits and to protect the same against voltage collapse, cascade tripping and tripping of important corridors / flow gates
Clause

## Slide 27: Demand Estimation
Demand estimation for operational purposes is to be done on a daily/weekly/monthly basis initially, mechanism and facilities at SLDCs shall be created at the earliest but not later than 1.1.2011 to facilitate on-line estimation of demand for daily operational use for each 15 minutes block.
The monthly estimated demand by the SLDC shall be provided to RLDC and RPC
The SLDC shall take into account the Wind Energy forecasting to meet the active and reactive power requirement.
In order to facilitate estimation of Total Transfer Capability / Available Transfer Capability on three month ahead basis , the SLDC shall furnish estimated demand and availability data to RLDCs.
Clause

## Slide 28: Demand side Management
Contingency Procedure that enable demand disconnection as instructed by RLDC / SLDC under normal and / or contingent condition
State Electricity Boards/Distribution Licensees shall also formulate and implement state-of-the-art demand management schemes for automatic demand management like rotational load shedding, demand response (which may include lower tariff for interruptible loads) etc. before 01.01.2011. A Report detailing the scheme and periodic reports on progress of implementation of the schemes shall be sent to the Central Commission by the concerned SLDC.
Grouping of Loads by SLDC without overlapping between different Groups as given below
  Loads for scheduled power cuts/load shedding
  Loads for unscheduled load shedding
  Loads to be shed through under frequency relays/df/dt relays
  Loads to be shed under any System Protection Scheme identified at the RPC level.
Clause

## Slide 29: Communication System
Each User, STU, RLDC, NLDC and CTU shall provide and maintain adequate and reliable communication facility internally and with other Users / STUs / RLDC / SLDC to ensure exchange of data / information necessary to maintain reliability and security of the grid.
Clause

## Slide 30: Restoration Procedure
RLDC shall develop detailed plans and procedures for restoration of the regional grid under partial/total blackout and shall be reviewed / updated annually.
b) Detailed plans and procedures for restoration after partial/total blackout of each User’s/STU/CTU system within a Region, will be finalized by the concerned User’s/STU/CTU in coordination with the RLDC. The procedure will be reviewed, confirmed and/or revised once every subsequent year. Mock trial runs of the procedure for different subsystems shall be carried out by the Users/CTU/STU at least once every six months under intimation to the RLDC. Diesel Generator sets for black start would be tested on weekly basis and test report shall be sent to RLDC on quarterly basis.
c) List of generating stations with black start facility, inter-State / interregional ties, synchronizing points and essential loads to be restored on priority, shall be prepared and be available with NLDC, RLDC and SLDC.
Clause

## Slide 31: Scheduling Responsibility
RLDC has Scheduling Responsibility for
a) Central Generating Stations (excluding stations where full Share is allocated to host state),
b) Ultra-Mega power projects
c) If a generating station is connected only to the ISTS, (except for Central Generating Stations where full Share is allocated to one State)
d) If a generating station is connected to both ISTS and the State network and if the state has 50% Share of power or less ( of the generating capacity put into commercial operation)
SLDC has Scheduling Responsibility for
a) Generating station which is connected only to the State transmission network
b) Central Generating Station whose full Share is allocated to host state.
c) If a generating station is connected both to ISTS and the State network and if the state has more than 50% Share of power (of the generating capacity put into commercial operation)
d) Generating station supplying power to any state other than host state

## Slide 32: Scheduling Responsibility
NLDC shall be responsible for
scheduling and despatch of electricity over inter-regional links in accordance with the grid code specified by Central Commission in coordination with Regional Load Despatch Centers.
NLDC shall be responsible for coordination with Regional Load Despatch Centers for the energy accounting of inter-regional exchange of power.
NLDC shall also be responsible for coordination for trans-national exchange of power.
NLDC shall develop a procedure for scheduling of collective transaction through Power Exchanges, scheduling of inter-regional power exchanges including HVDC setting responsibility and power exchanges of the country with other countries., ,

## Slide 33: Cont..
All concerned entities (in whose premises the special energy meters are installed) shall take weekly meter readings and transmit them to the RLDC by Tuesday noon The SLDC must ensure that the meter data from all installations within their control area are transmitted to the RLDC within the above schedule.
Deviations, if any, from the ex-power plant generation schedules / ex-boundary drawal schedule shall be appropriately priced in accordance with UI Regulations. In addition, deviations, from schedules causing congestion, shall also be priced in accordance with the Congestion Charge Regulations. of CERC
The operating log books of the generating station shall be available for review by the Regional Power Committee. These books shall keep record of machine operation and maintenance.

## Slide 34: Revision of Schedule (LTOA & MTOA)
In the event of system constraint the RLDC shall suo-mottu revise the schedules which shall become effective from the 4th time block. Also, during the first, second and third time blocks of such an event, the scheduled generation of the ISGS shall be deemed to have been revised to be equal to actual generation
Revision of declared capability by the ISGS(s) having two part tariff with capacity charge and energy charge (except hydro stations) and requisition by beneficiary(ies) for the remaining period of the day shall also be permitted with advance notice. Revised schedules/declared capability in such cases shall become effective from the 6th time block,

## Slide 35: Revision of STOA on real time operation
Notwithstanding anything contained in Regulation 6.5(18), in case of forced outage of a unit for a Short Term bilateral transaction, where a generator of capacity of 100 MW and above is seller, the generator shall immediately intimate the same along with the requisition for revision of schedule and estimated time of restoration of the unit, to SLDC/RLDC as the case may be. With the objective of not affecting the existing contracts, the revision of schedule shall be with the consent of the buyer till 31.07.2010.
Thereafter , consent of the buyer shall not be a pre-requisite for such revision of schedule. The schedule of the generator and the buyer shall be revised, accordingly. The revised schedules shall become effective from the 4th time block, counting the time block in which the forced outage is declared to be the first one.. The RLDC shall inform the revised schedule to the seller and the buyer. The original schedule shall become effective from the estimated time of restoration of the unit. However the transmission charges as per original schedule shall continue to be paid for two days.

## Slide 36: Scheduling of Wind Generation
With effect from 1.1.2011 Scheduling of wind power generation plants would have to be done for the purpose of UI where the sum of generation capacity of such plants connected at the connection point to the transmission or distribution system is 10 MW and above and connection point is 33 KV and above, and where PPA has not yet been signed.
The schedule by wind power generating stations may be revised by giving advance notice to SLDC/RLDC, as the case may be. Such revisions by wind power generating stations shall be effective from 6th time-block ,the first being the time –block in which notice was given. There may be maximum of 8 revisions for each 3 hour time slot starting from 00:00 hours during the day.

## Slide 37: 5.2(u) Special requirements for Solar/ wind generators
(u) Special requirements for Solar/ wind generators
System operator (SLDC/ RLDC) shall make all efforts to evacuate the available solar and wind power and treat as a must-run station. However, System operator may instruct the solar /wind generator to back down generation on consideration of grid security or safety of any equipment or personnel is endangered and Solar/ wind generator shall comply with the same. For this, Data Acquisition System facility shall be provided for transfer of information to concerned SLDC and RLDC
SLDC/RLDC may direct a wind farm to curtail its VAr drawl/injection in case the security of grid or safety of any equipment or personnel is endangered.
(ii) During the wind generator start-up, the wind generator shall ensure that the reactive power drawl (inrush currents incase of induction generators) shall not affect the grid performance.

## Slide 38: 23 . Special dispensation for scheduling of wind and solar generation
i) With effect from 1.1.2011 Scheduling of Solar power generation plants (5 MW and above and connection point is 33 KV where PPA has not yet been signed)
In case of solar generation no UI shall be payable/receivable by Generator.
ii) The schedule of solar generation shall be given by the generator based on availability of the generator, weather forecasting, solar insolation, season and normal solar generation curve and shall be vetted by the RLDC

## Slide 39: Reactive Power Management
The charge for VArh shall be at the rate of 10 paise/kVArh w.e.f. 1.4.2010, and this will be applicable between the Regional Entity, except Generating Stations, and the regional pool account for VAr interchanges. This rate shall be escalated at 0.5paise/kVArh per year thereafter, unless otherwise revised by the Commission.
In general, the Regional Entities except Generating Stations shall endeavor to minimize the VAr drawal at an interchange point when the voltage at that point is below 95% of rated, and shall not return VAr when the voltage is above 105%. ICT taps at the respective drawal points may be changed to control the VAr interchange as per a Regional Entity except Generating Stations’s request to the RLDC, but only at reasonable intervals.
Switching in/out of all 400 kV bus and line Reactors throughout the grid shall be carried out as per instructions of RLDC. Tap changing on all 400/220 kV ICTs shall also be done as per RLDCs instructions only.

## Slide 40: Other Important Features
Control Area Defined
Neighboring Country defined as a separate control area
Provision for reporting consistent Non-compliance of constituents to CERC directly by RLDC
Functions of NLDC defined. NLDC shall supervise inter regional links
SLDCs shall also develop Operating Procedure for real time grid operation.
Prolonged outage of power system elements shall be monitored by RLDC and report to RPC for suitable action.
Special exemption limit on UI volume for wind and other renewable energy generation

## Slide 41: Draft IEGC 2020
Grid code a dynamic document
  Evolving over time recognizing the current operating environment,
  future mix of energy-resources,
  technological advancements and the maturity of the system
First Grid Code prepared in 1999
  Beginning 2000, Indian electricity grid operating at four independent frequencies.
  Grid has expanded and grown rapidly and has been strongly integrated in to one synchronous grid operating at a common frequency since 2014.
  It has increased the grid stability and its capacity to accommodate the variability of renewable generation. Meeting a demand of 180 GW.
  The nominal operating frequency band has been progressively narrowed
  Deviations from the schedules checked,
    significantly controlling frequency excursions.

## Slide 42: Measures to strengthen grid security
Proposes measures to strengthen grid security and resilience
  Emphasis on flexibility of resources
  Ensuring automatic response to frequency excursions, grid security, reliability and renewable integration are technically feasible
covering all facets of power system planning
  Demand forecasting,
  Generation resource planning (flexibility, ramping, minimum turndown level),
  requirements of energy storage system,
  system reserves, system inertia for grid stability,
  inter-state system planning (including reoptimization system study, adequacy,
  enhancement of total transfer capability (TTC) across inter-regional boundaries as well as ISTS interfaced with STU network).

## Slide 43: Connection, protection and commissioning code
To be applicable to the generators and transmission licensees.
  This code specifies the requirements to be fulfilled by the connectivity grantees prior to obtaining the permission of the RLDC/NLDC/SLDC for first time energizing of a new or modified power system element.
  Technical requirements to be complied by a transmission licensee including deemed transmission licensees or cross-border entity prior to being allowed by RLDC/NLDC/SLDC to energize a new or modified power system element. The code also specifies the tests required before trial run.
A centralized data base containing details of relay setting for grid elements
  shall be maintained by RPC
  system wide study twice a year for validating the protection setting
  annual self-audit and third party once in five years.
  procedure for trial run and declaration of CoD for renewable generators

## Slide 44: Frequency response measures
Frequency response measures
  to correct the load generation imbalances in an automated manner
  with the help of primary, secondary and tertiary reserves
  coupled with demand response as a last resort.
In view of the comfortable power supply position, it is now possible to have reserve generating capacity on bar for a quick response.
  NLDC has already done the preparatory work with regard to AGC.
  initial or primary response at the rate of about 12–14 GW/Hz to contain frequency excursions.
  free governor mode of operation (FGMO) for all generating units in the country in order to arrest steap fall in the frequency in the event of a major grid disturbances.
  The primary response to be provided by the generating machines immediately up to five minutes
    by which time the secondary response shall take over through automatic generation control to recover the frequency.

## Slide 45: Monitoring of availability of reserve capacity
Quantum of reserve capacity
  required to be maintained for grid security
  Related to credible contingency
  Net error in the forecasts of demand and renewable generation.
Demand forecasting activity has been properly organized and there is a monitoring mechanism for errors in demand forecasting.
The operating code provides for ensuring and monitoring of availability of reserve capacity.

## Slide 46: Role of QCA
to minimize forecasting errors of renewable generators, aggregation of renewable energy has been allowed at one or more pooling stations for the purpose of deviation settlement.
An institutional mechanism, qualifed coordinating agency (QCA) for the composite scheduling and common deviation settlement of renewable generating stations at one or more pooling stations has been provided.
The role and functions of QCA has been specified in the Grid Code.

## Slide 47: Other provisions
nominal frequency band has been narrowed from 49.90- 50.05 Hz to 49.95-50.05 Hz band.
The power system condition has been categorized in to normal, alert, emergency, extreme emergency and restoration state.
The role of users has been defined for each state.
Structured demand estimation for operational planning studies has been described on daily, monthly and yearly basis.
The draft IEGC 2020 mandates adequacy of generation resources for round the clock supply to all consumer categories.
It proposes load shedding through demand response contracts or through special protection schemes in the event of an emergency situation.

## Slide 48: Provisions for renewables
Wind, solar, wind-solar hybrid and hydro plants (in case of excess water leading to spillage) shall be treated as MUST RUN power plants and shall not be subjected to curtailment on account of merit order despatch or any other commercial consideration.
In the event of transmission or system security constraint, the renewable generation may be curtailed after harnessing available flexible resources including energy storage systems.
Flexibility has been granted to the distribution utilities/ buyers having long-term transmission access for scheduling power out of their basket of power purchase agreements, including short-term contracts, up to the approved quantum of LTA.
This will facilitate the distribution utilities to optimize their power procurement cost.
Distribution utilities/ buyers having short-term bilateral access shall be able to revise their schedule as per the same timelines provided for the long-term or medium-term schedule.

## Slide 49: Flexibility of coal, lignite and gas based thermal generating stations
With a view to enhancing the flexibility of coal, lignite and gas based thermal generating stations for the emerging scenarios of high renewable energy penetration the compensatory mechanism for below the normative plant load factor has been reviewed
and rationalized.
The compensation for degradation in performance parameters resulting in higher cost of energy shall be calculated for each time block and settled on monthly basis. However, the extant mechanism has been retained for sharing of efficiency gain for power plants.

## Slide 50: Cyber Security
A new Code namely, Cyber Security has been added. The code provides for identification of Critical Information Infrastructure, appointment of Information Security Officer as per the Information Technology Rules 2018 and take necessary measures in accordance with guidelines by National Critical Information Infrastructure Protection Centre.

## Slide 51: List of references (taken from the Report of the expert committee to review IEGC)

## Slide 52
Thank you